{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Disclaimer","Anschlussleitungen","Verteilleitungen","Hauptleitungen"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Disclaimer","index":0,"n_rows":11,"n_cols":2,"rows_kept":11,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Die Berechnungshilfe wurde sorgfältig erstellt und auf Richtigkeit geprüft. "]
[null,"Für eine fehlerfreie Funktion kann dennoch nicht garantiert werden."]
[null,"Eine Haftung des Erstellers wird hiermit ausdrücklich ausgeschlossen."]

{"sheet":"Anschlussleitungen","index":1,"n_rows":30,"n_cols":10,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
[]
["Berechnung Druckluftnetz"]
["Anschlussleitungen"]
[]
["Bauvorhaben:",null,"Tierklinik Oberhaching"]
[]
["Projekt-Nr.:",null,"11-25"]
[]
["Datum:",null,"2012-01-26"]
[]
[]
["Teilstrecke",null,6,7,8,9,13,14,16,17]
[]
["Leitungsdurchmesser Vorauswahl","DN",12,12,12,12,12,12,12,12]
["Versorgungsüberdruck","pÜ in bar",15,15,15,15,15,15,15,15]
["Betriebstemperatur","TB in °C",20,20,20,20,20,20,20,20]
["Druckluftbedarf","VN in Nm³/h",1.5,1.5,1.5,1.5,1.5,1.5,1.5,5.6]
["Gleichzeitigkeit",null,1,1,1,1,1,1,1,1]
["Mittlere Einschaltdauer","ED",0.5,0.5,0.5,0.5,0.5,0.5,0.5,0.5]
["Zuschlag für Leckage","v",0.05,0.05,0.05,0.05,0.05,0.05,0.05,0.05]
["Reserve für Erweiterung","r",0,0,0,0,0,0,0,0]
["Volumenstrom","VN in Nm³/h",{"$f":"(C17*C18*C19)*(1+C20)","v":0.78750000000000009},{"$f":"(D17*D18*D19)*(1+D20)","v":0.78750000000000009},0.78750000000000009,0.78750000000000009,0.78750000000000009,0.78750000000000009,0.78750000000000009,2.94]
["Betriebsvolumenstrom","VB in Nm³/h",{"$f":"C22*1.01325*(273+C16)/(C15+1.01325)/273","v":5.3480155856508262E-2},{"$f":"D22*1.01325*(273+D16)/(D15+1.01325)/273","v":5.3480155856508262E-2},5.3480155856508262E-2,5.3480155856508262E-2,5.3480155856508262E-2,5.3480155856508262E-2,5.3480155856508262E-2,0.19965924853096415]
["Fließgeschwindigkeit","v in m/s",{"$f":"C23/3600/(POWER(C14/1000,2)/4*PI())","v":0.13135233274518929},{"$f":"D23/3600/(POWER(D14/1000,2)/4*PI())","v":0.13135233274518929},0.13135233274518929,0.13135233274518929,0.13135233274518929,0.13135233274518929,0.13135233274518929,0.49038204224870663]
["Druckverlust","R in mbar/m",0.02,0.02,0.02,0.02,0.02,0.02,0.02,0.04]
["Länge der Teilstrecke","l in m",3.5,2,2,5,4,1.5,2.5,3.5]
["Zuschlag für Einbauten / Formteile","f",0.4,0.4,0.4,0.4,0.4,0.4,0.4,0.4]
["Druckverlust","dp in mbar",{"$f":"(C26*C25)+(C26*C25*C27)","v":9.8000000000000004E-2},{"$f":"(D26*D25)+(D26*D25*D27)","v":5.6000000000000001E-2},5.6000000000000001E-2,0.14000000000000001,0.112,4.1999999999999996E-2,7.0000000000000007E-2,0.19600000000000001]
[]
["maximal erlaubter Druckverlust in Verteilleitung: 0,03 bar"]

{"sheet":"Verteilleitungen","index":2,"n_rows":32,"n_cols":9,"rows_kept":32,"cut":false,"hidden":false,"merged":[]}
[]
["Berechnung Druckluftnetz"]
["Verteilleitungen"]
[]
["Bauvorhaben:",null,"Tierklinik Oberhaching"]
[]
["Projekt-Nr.:",null,"11-25"]
[]
["Datum:",null,"2012-01-26"]
[]
[]
["Teilstrecke",null,3,4,5,10,11,12,15]
[]
["Leitungsdurchmesser Vorauswahl","DN",12,12,12,12,12,12,12]
["Versorgungsüberdruck","pÜ in bar",15,15,15,15,15,15,15]
["Betriebstemperatur","TB in °C",20,20,20,20,20,20,20]
["Druckluftbedarf","VN in Nm³/h",6,4.5,3,4.5,10.08,3,7.08]
["Gleichzeitigkeit",null,0.86,0.89,0.94,0.89,0.65,0.94,0.85]
["Mittlere Einschaltdauer","ED",0.5,0.5,0.5,0.5,0.5,0.5,0.5]
["Zuschlag für Leckage","v",0.05,0.05,0.05,0.05,0.05,0.05,0.05]
["Reserve für Erweiterung","r",0,0,0,0,0,0,0]
["Volumenstrom","VN in Nm³/h",{"$f":"(C17*C18*C19)*(1+C20)","v":2.7090000000000001},{"$f":"(D17*D18*D19)*(1+D20)","v":2.1026250000000002},1.4804999999999999,2.1026250000000002,3.4398000000000004,1.4804999999999999,3.1594500000000001]
["Betriebsvolumenstrom","VB in Nm³/h",{"$f":"C22*1.01325*(273+C16)/(C15+1.01325)/273","v":0.1839717361463884},{"$f":"D22*1.01325*(273+D16)/(D15+1.01325)/273","v":0.14279201613687706},0.10054269301023551,0.14279201613687706,0.23360132078122806,0.10054269301023551,0.21456238529631114]
["Fließgeschwindigkeit","v in m/s",{"$f":"C23/3600/(POWER(C14/1000,2)/4*PI())","v":0.45185202464345109},{"$f":"D23/3600/(POWER(D14/1000,2)/4*PI())","v":0.35071072842965539},0.2469423855609558,0.35071072842965539,0.57374698943098679,0.2469423855609558,0.52698555897369947]
["Druckverlust","R in mbar/m",0.04,0.03,0.02,0.03,0.05,0.02,0.04]
["Länge der Teilstrecke","l in m",15,8,2,15,15,8,3]
["Zuschlag für Einbauten / Formteile","f",0.4,0.4,0.4,0.4,0.4,0.4,0.4]
["Druckverlust","dp in mbar",{"$f":"(C26*C25)+(C26*C25*C27)","v":0.84},{"$f":"(D26*D25)+(D26*D25*D27)","v":0.33599999999999997},5.6000000000000001E-2,0.62999999999999989,1.05,0.224,0.16799999999999998]
[]
["Druckverlust kumuliert","dpges in mbar",{"$f":"D30+C28","v":1.232},{"$f":"E30+D28","v":0.39199999999999996},{"$f":"E28","v":5.6000000000000001E-2},{"$f":"G30+F28","v":1.9039999999999999},{"$f":"H30+G28","v":1.274},{"$f":"H28","v":0.224},{"$f":"I28","v":0.16799999999999998}]
[]
["maximal erlaubter Druckverlust in Verteilleitung: 0,03 bar"]

{"sheet":"Hauptleitungen","index":3,"n_rows":32,"n_cols":4,"rows_kept":32,"cut":false,"hidden":false,"merged":[]}
[]
["Berechnung Druckluftnetz"]
["Hauptleitungen"]
[]
["Bauvorhaben:",null,"Tierklinik Oberhaching"]
[]
["Projekt-Nr.:",null,"11-25"]
[]
["Datum:",null,"2012-01-26"]
[]
[]
["Teilstrecke",null,1,2]
[]
["Leitungsdurchmesser Vorauswahl","DN",12,12]
["Versorgungsüberdruck","pÜ in bar",15,15]
["Betriebstemperatur","TB in °C",20,20]
["Druckluftbedarf","VN in Nm³/h",20.58,10.5]
["Gleichzeitigkeit",null,0.86,0.86]
["Mittlere Einschaltdauer","ED",0.5,0.5]
["Zuschlag für Leckage","v",0.05,0.05]
["Reserve für Erweiterung","r",0,0]
["Volumenstrom","VN in Nm³/h",{"$f":"(C17*C18*C19)*(1+C20)","v":9.2918699999999994},{"$f":"(D17*D18*D19)*(1+D20)","v":4.7407500000000002}]
["Betriebsvolumenstrom","VB in Nm³/h",{"$f":"C22*1.01325*(273+C16)/(C15+1.01325)/273","v":0.6310230549821122},{"$f":"D22*1.01325*(273+D16)/(D15+1.01325)/273","v":0.3219505382561797}]
["Fließgeschwindigkeit","v in m/s",{"$f":"C23/3600/(POWER(C14/1000,2)/4*PI())","v":1.5498524445270372},{"$f":"D23/3600/(POWER(D14/1000,2)/4*PI())","v":0.79074104312603943}]
["Druckverlust","R in mbar/m",0.25,0.09]
["Länge der Teilstrecke","l in m",2,2]
["Zuschlag für Einbauten / Formteile","f",0.4,0.4]
["Druckverlust","dp in mbar",{"$f":"(C26*C25)+(C26*C25*C27)","v":0.7},{"$f":"(D26*D25)+(D26*D25*D27)","v":0.252}]
[]
["Druckverlust kumuliert","dpges in mbar",{"$f":"D28+C28","v":0.95199999999999996}]
[]
["maximal erlaubter Druckverlust in Hauptleitung: 0,04 bar"]